# SMART COIL SPECIFICATION DATA

## Only applicable for Fluid and Steam Coils with Cooney Freeze Block Technology

- Provide fluid or steam coil with Cooney Freeze Block Technology

- An adapter fitting will be attached to the bottom of every Cooney Freeze Block relief valve (plain end or hose barb)

  - Material designed to handle temperatures from -40F to 300F

  - Material must be non-conductive

  - Adapter fitting will house a conductivity sensor designed to sense when the Cooney Freeze Block relief valve discharges during a freezing event

  - Must be designed to only sense water from valve discharge and not from environment

  - Must not hold water after valve deployment

- Sensor is wired to the supplied control box terminal strip

- Standard NEMA 4 rated Control box to allow an input voltage range of 24 – 305 VAC single phase

- Output shall be through a relay switch to the Building Automation System and/or Air handling unit controls

- BAS (Building Automation System) to then be programmed to perform, but not limited to, the following sequence of operations:

  - Turn off power to the fan

  - Close Outside Air Dampers

  - Activate steam or water flow to preheat coil – where applicable

  - Send alarm to control center to notify maintenance personnel

  - Local Audible/Visual Alarm (optional)